GEO-SEAL EV80 SLAB ON GRADE EVOH COMPOSITE VAPOR INTRUSION BARRIER SPECIFICATION VERSION 1.0

SECTION 02 56 16 – GAS CONTAINMENT

SECTION 02 56 19.13 – FLUID-APPLIED GAS BARRIER

General

  - Related documents

Drawings and general provisions of the contract, including general and supplementary conditions, and Division 1 specification section, apply to this section.

section includes

The installation of materials designed to provide vapor intrusion protection when installed per project specification, this section covers the methane mitigation and vapor intrusion membrane, along with the following:

Surface preparation and substrate treatment

Auxiliary materials

Prefabricated drainage mat (if applicable)

Foundation drain (if applicable)

Related Sections

Section 02 24 00: Environmental Assessment

Section 02 32 00: Geotechnical Investigation

Section 03 15 00: Concrete Accessories

Section 03 30 00: Cast-in-Place Concrete

Section 03 40 00: Precast Concrete

Section 07 90 00: Joint Protection

Section 31 30 00: Earthwork Methods

Section 33 41 00: Subdrainage

Performance requirements

General: Provide a vapor mitigation system that prevents the passage of methane gas, contaminant vapors including chlorinated solvents and petroleum hydrocarbons, and complies with the physical requirements as demonstrated by testing performed by an independent testing agency.

Submittals

Product Data: Submit manufacturer's printed technical data, tested physical and performance properties, instructions for evaluating, preparing, and treating substrates, and installation instructions.

Shop Drawings: Project specific drawings showing locations and extent of vapor intrusion barrier system, details for overlaps, penetrations, transitions, and termination conditions.

Samples: Submit two standard size samples of the each of the following:

Individual components of the specified composite vapor intrusion barrier system.

Applicator Certification:  Submit written confirmation at the time of bid that applicator is currently approved by the membrane manufacturer.

quality assurance

Applicator Qualifications: System applicator shall be an EPRO Authorized Applicator who is trained to perform work that is in accordance with EPRO standards and policies.

Manufacturer Qualification: Obtain vapor intrusion barrier materials and system components from a single manufacturer source, EPRO. Manufacturer must have 20 years of experience in the manufacture of vapor intrusion barrier systems.

Third Party Inspection: Independent inspection of the composite system installation may be required based on project conditions and desired warranty coverage, or as required based on local building code/government agency jurisdiction. Inspection reports shall be submitted directly to the composite vapor intrusion barrier manufacturer and made available to other parties per the owner’s direction.

Pre-Construction Meeting: A meeting shall be held prior to application of the barrier system to assure proper substrate preparation, confirm installation conditions, and any additional project specific requirements. Attendees of the meeting shall include, but are not limited to the following:

EPRO authorized applicator

Third party inspector

General contractor

Owner’s representative

Architect and Engineer

Concrete/Shotcrete contractor

Rebar contractor

All appropriate related trades

Field Sample: Apply vapor intrusion barrier system field sample to 100 ft2 (9.3 m2) of each assembly to demonstrate proper application techniques and standard of workmanship.

Notify composite membrane system manufacturer representative, architect, certified inspector, and other appropriate parties one week in advance of the dates and times when field sample will be prepared.

If architect and certified inspector determines that field sample does not meet requirements; reapply composite membrane system until field sample is approved.

Retain and maintain approved field sample during construction in an undisturbed condition as a standard for judging the completed composite membrane system.  An undamaged field sample may become part of the completed work.

delivery, storage and handling

Delivery: Deliver materials to site labeled with manufacturer's name, product brand name, material type, and date of manufacture.  Upon the arrival of materials to the jobsite, inspect materials to confirm material has not been damaged during transit.

Storage: Proper storage of onsite materials is the responsibility of the certified applicator. Consult product data sheets to confirm storage requirements. Storage area shall be clean, dry, and protected from the elements.  If ambient air temperatures are expected to fall below 40(F, precautions will need to be taken to protect any emulsion product from near freezing temperatures. Protect stored materials from direct sunlight.

Disposal: Remove and replace any material that cannot be properly applied in accordance with local regulations and specification section 01 74 19.

Project conditions

Substrate Review: Substrates shall be reviewed and accepted by the certified applicator and independent inspector prior to application.

Penetrations: All plumbing, electrical, mechanical, and structural items to be passing through the composite membrane system shall be properly spaced, positively secured in their proper positions, and appropriately protected prior to system application and throughout the construction phase. Braided grounding rods are not allowed to pass through the vapor intrusion barrier.

Reinforcement Steel and Concrete Forms: Vapor intrusion barrier shall be installed before placement of reinforcing steel. When penetrations post system installation occurs, it is the responsibility of the general contractor to notify the vapor intrusion barrier applicator to immediately make repairs prior to the placement of overburden, this includes the use of solid plastic “VaporStakes” used to secure concrete forms.

Clearance: Minimum clearance of 24 inches is required for application of spray applied polymer modified asphalt, Geo-Seal CORE.  For areas with less than 24-inch clearance, the product may be applied by hand using Geo-Seal CORE Detail.

Overspray: Protect all adjacent areas not receiving the barrier application. Masking is necessary to prevent unwanted overspray from adhering to, or staining, areas not receiving the membrane. Once Geo-Seal CORE adheres to a surface it is extremely difficult to remove.

Weather Limitations: Perform work only when existing and forecast weather conditions are within manufacturer's recommendations.

Spray Applied Polymer Modified Asphalt Membrane: Minimum ambient temperature should be 40(F (7(C) and rising. For applications temperatures below 38(F, but greater than +19ºF/-7ºC, special equipment and material handling is required.  Substrate shall be clean and free from standing moisture.

EPRO applicators reserve the right not to install product when application conditions might be within manufactures acceptance, but ambient conditions may limit a successful application.

Warranty

Special Warranty: Submit a written warranty signed by vapor intrusion barrier manufacturer agreeing to replace system materials that do not conform to manufacturer’s published specifications or are deemed to be defective.  Warranty does not include failure of vapor intrusion barrier due to failure of soil substrate prepared and treated according to requirements or formation of new joints and cracks in the concrete that exceed 1/8 inch (3.175 mm) in width.

Warranty Period: 1 years after date of substantial completion.  Longer warranty periods are available upon request.

Coverage: Manufacturer will guarantee that the material provided is free of defects for the warranty period.

Additional Warranty Options: Upgraded warranties are available by contacting the manufacturer.  These warranties may have additional requirements and approval must be granted in accordance to the manufacturer’s warranty requirements.  Additional warranty options include:

Standard Labor and Material (Geo-Seal L&M): Manufacturer will provide non-prorated coverage for the warranty term, agreeing to repair or replace material that does not meet requirements or remain vapor tight.

Waterproofing Warranties: For below grade projects that require vapor intrusion barriers and below grade waterproofing for foundation walls, single source warranties are available from EPRO.

- Products

manufacturers

Acceptable Manufacturer: EPRO Services, Inc. (EPRO), P.O. Box 347; Derby, KS 67037; Tel: (800) 882-1896; www.eproinc.com

Basis of Design: Geo-Seal EV80 (78 mils) – Geo-Seal EV30, Geo-Seal CORE (30 mils), Geo-Seal BOND

Vapor intrusion barrier materials

The physical properties listed in this section reflect testing on the entire composite system. Physical properties of the individual system composite can be found in Specification Section 2.3.

Geo-Seal EV80 Vapor Intrusion Barrier consists of a 30 mil layer of Geo-Seal CORE (polymer modified asphaltic membrane) sandwiched between two HDPE geocomposite membranes Geo-Seal EV30 layer and Geo-Seal BOND protection sheet. Geo-Seal is ideal for moisture protection on sites that may also contain methane gas, contaminated soil, or contaminated groundwater.

| PROPERTIES | TEST METHOD | VALUE |
| --- | --- | --- |
| Adhesion to Concrete | ASTM D903 | 8 lbf/in |
| Puncture Resistance | ASTM D1709 | 310 lbf |
| Water Vapor Transmission | ASTM E96 | 0.035 perms |
| Water Vapor Permeance | ASTM E96B | 0.14 grains/h-ft2 |
| PCE Diffusion Rate | Geokinetics | 1.62 x 10-17 m2/sec |
| Benzene Diffusion Rate | Geokinetics | 1.5 x 10-15 m2/sec |
| Vapor Barrier Classification | ASTM E1745 | A, B & C |
| Life Expectancy | ASTM E154 | Infinite |

Polymer Modified Asphalt

Geo-Seal CORE: Geo-Seal CORE is a non-hazardous, low-viscosity, water-based, anionic asphalt emulsion modified with a blend of synthetic polymerized rubbers and proprietary additives. Geo-Seal CORE is highly stable during transit and when properly stored but becomes highly reactive during the spray application to form a rapidly cured membrane with exceptional bonding, elongation, and hydrophobic characteristics.

| PROPERTIES | TEST METHOD | VALUE |
| --- | --- | --- |
| Color |  | Brown to Black |
| Solvent Content |  | No Solvents |
| Shelf Life |  | 6 months |
| Tensile Strength | ASTM 412 | 32 psi |
| Elongation | ASTM 412 | 4140% |
| Resistance to Decay | ASTM E 154 Section 13 | 4% Perm Los |
| Accelerated Aging | ASTM G 23 | No Effect |
| Moisture Vapor Transmission | ASTM E 96 | 0.026 g./sq. ft./hr. |
| Hydrostatic Water Pressure | ASTM D 751 | 26 psi |
| Perm Rating | ASTM E 96 (US Perms) | 0.21 |
| Methane Transmission Rate | ASTM D 1434 | 0 |
| Adhesion to Concrete & Masonry | ASTM C 836 & C 704 | 20 lbf./inch |
| Adhesion to HDPE | ASTM C 836 | 28.363 lbf./inch |
| Adhesion to Polypropylene Fabric | ASTM C 836 | 31.19 lbf./inch |
| Hardness | ASTM C 836 | 80 |
| Crack Bridging | ASTM C 836-00 | No Cracking |
| Low Temp. Flexibility |  | No Cracking at -20° C |
| Packaging: 55 gallon drum, 275 gallon tote, 330 gallon tote |

Geo-Seal CORE Detail: Geo-Seal CORE Detail is single component, medium viscosity, water-based, polymer-modified anionic asphalt emulsion, which exhibits exceptional bonding, elongation and hydrophobic characteristics.

| PROPERTIES | TEST METHOD | VALUE |
| --- | --- | --- |
| Color |  | Brown to Black |
| Solvent Content |  | No Solvents |
| Shelf Life |  | 6 months |
| Tensile Strength | ASTM 412 | 32 psi |
| Elongation | ASTM 412 | 3860% |
| Resistance to Decay | ASTM E 154 SECTION 13 | 9% Perm Loss |
| Accelerated Aging | ASTM G 23 | No Effect |
| Moisture Vapor Transmission | ASTM E 96 | 0.071 g/sq. ft./hr. |
| Hydrostatic Water Pressure | ASTM D 751 | 28 psi |
| Perm Rating | ASTM E 96 (US Perms) | 0.17 |
| Methane Transmission Rate | ASTM D 14334 | 0 |
| Adhesion to Concrete & Masonry | ASTM C 836 | 1 lbf/inch |
| Hardness | ASTM C 836 | 85 |
| Crack Bridging | ASTM C 836 | No Cracking |
| Low Temp. Flexibility | ASTM C 836-00 | No Cracking at -20° C |
| Packaging: 5 gallon bucket |

Geocomposite Base Sheet

Geo-Seal EV30: Geo-Seal EV30 is an extremely durable, high strength base course made from the lamination of EVOH film and nonwoven polypropylene geotextile fabric.

| PROPERTIES | TEST METHOD | VALUE |
| --- | --- | --- |
| Film Material |  | Polyethylene & EVOH |
| Film Color |  | White/Gray |
| Thickness |  | 31 Mil |
| Weight |  | 402.5 g/m2 |
| Classification | ASTM E1745 | Class A, B & C |
| Water Vapor Transmission | ASTM E96 | 0.014 grains/h-ft2 |
| Water Permeance | ASTM E96 | 0.035 perms (US) |
| Tensile Strength | ASTM D882 | 55 lbf |
| Puncture Resistance | ASTM D1709 | 2255 grams |
| Elongation | ASTM D882 | 587% |
| Life Expectancy | ASTM E 154 | Infinite |
| Methane Gas Permeance | ASTM D1434 | 3.68 x 10-12 m/s |
| Weight: 150 pounds |
| Dimensions: 12” x 150’ |

Geocomposite Protection Course

Geo-Seal BOND: Geo-Seal BOND is an extremely durable, high strength protection course made from the lamination of HDPE film and nonwoven polypropylene geotextile fabric.

| PROPERTIES | TEST METHOD | VALUE |
| --- | --- | --- |
| Film Material |  | HDPE |
| Film Color |  | White |
| Fabric Material |  | Non-woven Polypropylene |
| Fabric Color |  | White |
| Film Thickness |  | 5 Mil |
| Composite Thickness |  | 18 Mil |
| Tensile @ ULT | ASTM D 882 | TD 32.0 lbs/in |
|  |  | MD 37.3 lbs/in |
| Elongation @ ULT | ASTM D 882 | TD 65.3% |
|  |  | MD 51.0% |
| Dart Impact | ASTM D 1709 | Method A >1070 grams |
|  |  | Method B 894 grams |
| Modulus | ASTM D 882 | TD 270.6 lbs/in |
|  |  | MD 295.5 lbs/in |
| Elmendorf Tear | ASTM D 1922 | TD 5,140 grams |
|  |  | MD 5,260 grams |
| Puncture-Prop Tear | ASTM D 2582 | TD 13,250 grams Sled: 1-lb |
|  |  | MD 11,290 grams Sled: 1-lb |
| Beach Puncture Tear | ASTM D 751 | TD 165 in-lbs |
|  |  | MD 160 in-lbs |
| Water Permeance | ASTM E 96 | 0.11 perms (US) |
| Dimensions: 12' x 150' |
| Weight: 108 pounds |

Auxiliary Materials

      - General: All accessory products shall be provided by the specified vapor intrusion barrier manufacturer.  Auxiliary products used in lieu of, or in addition to, the manufacture’s products must be approved in writing by EPRO prior to installation.

Reinforcement Fabric: Manufacturer’s polyester fabric, Geo-Seal Reinforcement Fabric is available in 6 inch, 12 inch, and 40 inch widths.

Detailing Material: Geo-Seal CORE Detail, a roller applied, water based, high viscosity, polymer modified asphaltic material.

Backer Rod: Closed cell polyethylene foam

Termination Bar: e.term hd, or approved alternate

Execution

examination

Comply with project documents, manufacturer’s product information, including product application and installation guidelines, pre-job punch list, as well as, manufacturer’s shipping and storage recommendations.

Surface Preparation

The general contractor shall engage the certified vapor intrusion barrier contractor and certified inspector to ensure surfaces are prepared in accordance with manufacturer’s instructions.  Unless, explicitly stated in the contract documents, the vapor intrusion barrier contractor is not responsible for surface preparation.

Examine all substrates, areas, and conditions under which the composite membrane system will be installed, applicator and inspector must be present.  Do not proceed with installation until unsatisfactory conditions have been corrected and surface preparation requirements have been met.  If conditions exist that are not addressed in this section, notify inspector and contact EPRO for additional clarification.

Soil and Sand Substrates: Native soil and sand substrates shall be uniformly compacted to meet structural and building code requirements.  All surfaces shall be free from protrusions and debris that may compromise the membrane system. Free standing water must be removed prior to application.

Aggregate Substrates: Aggregate substrates shall be compacted to meet structural and building code requirements and then rolled flat to provide a uniform substrate.  ¾ inch minus aggregate with no more than one fractured face is recommended, but other aggregates substrates may be approved by the manufacturer provided they do not create sharp angular protrusions that may compromise the vapor intrusion system.

Working Slab: Mud slab, rat slab, or other concrete working slab shall have a uniform plane with a light broom or light trowel finish.

Concrete Surfaces: Clean and prepare concrete surface to manufacturer’s recommendations. In general, only apply the Geo-Seal CORE material to dry, clean and uniform concrete substrates with a light trowel, light broom, or equivalent finish.

Cast-in-Place or Shotcrete Walls: Application to green concrete is acceptable provided the substrate is prepared in accordance with manufacturers specifications and published instructions.

Provide clean, dust-free, and dry substrate for vapor intrusion barrier application.

Surfaces shall be power washed to remove grease, oil, form release agents, or any other penetrating contaminants from the concrete.

Remove all fins, ridges, and other protrusions.

Fill honeycomb, aggregate pockets, tie holes, and other voids with hydraulic cement, or rapid-set grout.

Vapor intrusion barrier installation

General: The underslab vapor intrusion system shall be installed under strict accordance with the manufacturer’s guidelines and project specifications.

    - GEOCOMPOSITE base course – Geo-Seal EV30

Whenever possible roll out Geo-Seal EV30, geotextile facing down, in the same direction over the substrate. When multiple pours will occur, extend the Geo-Seal EV30 a minimum of 2 feet past the pour joint.

Overlap Geo-Seal EV30 a minimum of 6 inches.

At the seam overlap, peel back the top layer of Geo-Seal EV30 and apply 60 mils into the overlapping seam, making certain to apply Geo-Seal CORE to both the top of the bottom sheet and the bottom of the top sheet. Embed the top sheet into the bottom sheet.

Visually verify there are no gaps/fish-mouths in seams.

Termination Sequence

System Termination: The termination process is appropriate for terminating the membrane onto exterior footings, pile caps, interior footings, and grade beams.  When terminating the membrane to stem walls or vertical surfaces the same process should be used.

Concrete surfaces that are not a light trowel, light broom or equivalent finish, will need to be repaired.

Terminations on horizontal and vertical surfaces should extend 6” onto the termination surface.  Job specific conditions may prevent a 6” termination.  In these conditions exist, contact manufacturer for recommendations.

Apply 60 mils of Geo-Seal CORE to the terminating surface and then embed the Geo-Seal EV30 layer by pressing it firmly into the Geo-Seal CORE layer.

Apply 30 mils of Geo-Seal CORE to the Geo-Seal EV30 layer.

Apply the Geo-Seal BOND layer and apply a final 30 mil seal of the Geo-Seal CORE layer over the edge of the termination.  For further clarification, refer to the termination detail provided by manufacturer.

Sealing of penetrations

Sealing of Standard Pipe Penetrations: Prepare membrane penetrations so they are free of any material that will inhibit a direct bond to the penetration surface: foam, insulation, protective coatings, etc.

Trim Geo-Seal EV30 to within 1/8 inch of the penetration.

Apply Geo-Seal CORE Detail 3 inches horizontally and 3 inches vertically around the base of the penetration.

Embed Geo-Seal Reinforcement Fabric reinforcement fabric 3 inches horizontally and 3 inches vertically around the base of the penetration.

Apply a second layer of Geo-Seal CORE Detail to reinforcement fabric until the reinforcement fabric is fully saturated. Secure Geo-Seal Reinforcement Fabric reinforcement fabric to penetration with a cable tie. For further clarification, refer to the termination detail provided by manufacturer.

polymer modifed asphalt membrane – geo-Seal CORE

Mask off adjoining surfaces where unwanted Geo-Seal CORE polymer modified asphalt membrane may be exposed on finished surfaces or impact other construction trades.

Commence application of Geo-Seal CORE polymer modified asphalt when ambient air temperatures are within manufacturer recommendations.

Surfaces that will receive the membrane must be clean and free from standing moisture.

Start installing Geo-Seal CORE in presence of approved 3rd party inspector or required city inspector.

Apply one application of Geo-Seal CORE membrane in accordance to manufacturer’s instructions in order to obtain a seamless membrane with a minimum dry film thickness of 30 mils (1.5 mm).

Apply Geo-Seal CORE/Geo-Seal CORE Detail in and around penetrations and cavities to ensure the formation of monolithic seal around all penetrations.

Apply Geo-Seal CORE/Geo-Seal CORE Detail to prepared wall terminations and vertical surfaces to heights indicated according to manufacturer’s recommendations and details. (if applicable)

Verify Geo-Seal CORE thickness of every 1000 ft2 (93 m2), or as required by specifying engineer.

Geocomposite protection course – Geo-Seal BOND

Sweep off any water that has collected on the surface of the Geo-Seal CORE layer, prior to the placement of the Geo-Seal BOND layer. Install Geo-Seal BOND protection course perpendicular to the direction of the Geo-Seal BASE.

Overlap Geo-Seal BOND seams a minimum of 6 inches.

Secure the seams of Geo-Seal BOND by applying 30 mils of Geo-Seal CORE in-between the seam overlap OR by applying a 30 mil layer of Geo-Seal CORE on top of the seam overlap, completely covering the seam overlap.

To expedite the construction process, the Geo-Seal BOND layer can be placed over the Geo-Seal CORE immediately after the spray application is complete, provided the Geo-Seal CORE mil thickness has been verified and smoke tested.

Do not penetrate the membrane system once it has been applied. If the vapor intrusion barrier is penetrated, immediately contact the applicator.  Failure to bring the breach of the membrane to the applicators attention and not allowing adequate time to make the necessary repair will result in voidance of warranty.

field quality control

Smoke Test: Conduct smoke test on all underslab areas upon installation of the Geo-Seal EV30 sheet, the sealing of all penetrations, and application of Geo-Seal CORE. All deficient areas shall be noted, marked for repair, and repairs verified. Refer to manufactures smoke testing protocol for additional guidance.

For projects that will require a Labor and Material warranty, certified 3rd party inspector is required to inspect and verify the integrity of the membrane

Field Inspection: Contact EPRO for independent certification process.

Thickness Verification: Use a digital mil reading caliper to measure the thickness of coupon samples. To measure coupon samples correctly, the thickness of the systems Geo-Seal EV30 layer must be measured in the field and taken into account when verifying coupon sample thicknesses.  Mark coupon sample area for repair. Contact EPRO for coupon sampling protocol.

It should be noted that taking too many destructive samples can be detrimental to the membrane.  Areas where coupon samples have been removed need to be marked for repair.

Take care to prevent contamination and damage during application stages and curing. Machinery, additional trades, or general construction shall NOT take place over the membrane until inspection is complete and concrete has been placed.  The membrane shall always be properly protected when equipment is operated near the membrane.

Prevent damage during the placement of reinforcement steel and overburden.

Damage Observation: Prior to the placement of concrete a visual inspection to confirm no damage has occurred from construction traffic or during the placement of reinforcement steel is recommended.

Repairs

Underslab:

Inspect damaged area to determine which system components have been damaged.

If the Geo-Seal EV30 sheet has not been compromised, patch only the areas that have been damaged by re-installing the damaged materials. The patch should extend 6 inches beyond the damaged area in all directions.

If the Geo-Seal EV30 sheet has been breached but no additional system components have been installed, install a patch below and above the base sheet that extends 6 inches beyond the damaged area. Area shall be sealed using the specified method for sealing the base sheet.

If the damaged area has breached the base sheet and additional components have been installed over the Geo-Seal EV30 sheet, the area will require removal of the overlying components to expose the Geo-Seal EV30 sheet.

If the damage is less than 3 inches, the base sheet will need to be opened up to create a minimum 4-inch diameter circle to allow access

Place a minimum 8-inch diameter coupon under the base sheet and seal using the specified method for seaming the base sheet. If heat welding the seam, probe the seam to ensure a uniform seal.

Apply a reinforcement detail of Geo-Seal CORE Detail and reinforcement fabric 6 inches beyond the edge of the repair area.

Apply the remaining layers as specified.

Refer to manufacturer’s detail for further repair clarification.

End of Section

# Text boxes

Applications: 	Slab On Grade Gas Containment Composite Vapor Intrusion Barrier

Spec Version: 	EproGSEV80.VB.v1.08.20gs

Date issued:	September 22, 2020

Note:	This specification may be superseded at any time.  Check eproinc.com for the most up to date version of this specification.

SECTION 02 56 16

GAS CONTAINMENT

SECTION 02 56 19.13

FLUID APPLIED GAS BARRIER

Geo-Seal EV80 EVOH

Composite Vapor Intrusion Barrier

Guide Specification

Slab On Grade

Geo-Seal EV80 is a 79 mil thick composite membrane that combines Ethylene Vinyl Alcohol (EVOH), HDPE, and spray-applied polymer modified asphalt to create a composite vapor intrusion barrier system to address a wide range of project conditions and contamination. This guide specification has been prepared according to the principles established in the Manual of Practice published by the Construction Specification Institute.

Note: If areas will be subjected to water and/or hydrostatic conditions, contact EPRO for appropriate system recommendations.

For additional questions, your local EPRO technical representative can be contacted through: EPRO Services, Inc., Wichita KS; 1.800.882.1896; www.eproinc.com.